## Announcement 
differential pressure transmitter PS 27

Compact differential pressure transmitter for basic applications

- Measurement ranges from 0..50 Pa to 100 kPa

- Either with one fixed measurement range or toggling between four different measurement ranges

- For measuring positive or negative pressures, even asymmetrically

- Also available with two-wire technology (optional)

- Measurement ranges and output signals can be selected via jumpers (optional)

- Can be calibrated

- With 1 alarm contact (optional)

- With LCD (optional)

- Top-hat rail mounting and wall surface installation IP 65

Technical data

Measurement

ranges:	50/100/200/500 Pa,

1/2.5/5/10/20/50/100 kPa

(others on request)

Analog outputs: 	0..10 V, 2..10 V, 
0..20 mA, 4..20 mA, 
0..5 V

Power supply:	24 VAC/ DC, ±10 %
15..32 VDC (two-wire)

LCD: 	4-digit (optional)

Contact points: 	1 switching relay

max. 230 VAC, 6 A

Margin of error: 	2 % of the set value for

≥ 100 Pa or

3 % of the set value for 50 Pa

Temperature
coefficient span:	0.1 % of max. value / K

Temperature 
coefficient

zero point:	0.1 % of max. value / K

Max. system

pressure:	10 kPa for measuring ranges ≤ 10 kPa

max. nominal pressure of sensor for measurement ranges above 10 kPa

overload capacity: 	12 x for measurement ranges ≤ 20 kPa

4 x for measurement ranges ≥ 20 kPa

Medium: 	Air, all non-aggressive gases

Sensor 
response time: 	20 ms

Time constant: 	20 ms .. 4 s adjustable

(factory-provided)

Operating

temperature:	-20..60°C

with display 0..50 °C

Storage

temperature: 	-20..70 °C

Power
consumption: 	approx. 1 VA

Weight: 	approx. 0.25 kg

Cable glands: 	2 x M 12

Pressure ports: 	for tubing NW 4-6 mm

Protection class: 	IP 65

Housing/ cover: 	ABS

Dimensions: 	80 mm x 87 mm x 52 mm

Wall mounted

housing: 	Top-hat rail assembly and wall mounting possible

Certificates: 	CE

Optional: 	DAkkS calibration certificate,

ISO factory calibration certificate

Designation:	differential pressure transmitter

Type: 	PS 27

Manufacturer: 	halstrup-walcher GmbH